## Hertz
"Hertz" A Variable Frequency Calculator & Plotter "with Autoplot"
| Joe Evans, Ph.D 6/22/02 Updated 12/15/04 |  |  |  |  | http://www.pumped101.com
MULTIPOINT CALCULATOR
Instructions are located directly below each calculator
[11 empty] | ENTER THE DESIRED SYSTEM CURVE HEADS IN | [7 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
FEET IN CELLS V14 - AC14.
| AFFINITY LAW CALCULATOR |  |  |  |  | SINGLE POINT CALCULATOR
| ENTER RPM IN CELL B22 |  |  |  |  | ENTER FLOW, HEAD (IN FT), |  |  |  |  | ENTER UP TO EIGHT 60 HERTZ FLOWS IN CELLS N22 - U22 STARTING WITH 0
[6 empty] | & HP IN CELLS H22, I22, & K22 |  |  |  |  | ENTER CORRESPONDING HEADS IN IN FEET IN CELLS V22 - AC22
HERTZ | RPM | D Q | D H | D HP | HZ | Q (GPM) | H (FT) | H (PSI) | P (HP) | HZ | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
60 | 3450 | 100% | 100% | 100% | 60 | 100 | 200 | 86.5801 | 7.5 | 60 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 485 | 480 | 462 | 450 | 427 | 404 | 375 | 335
59 | 3392.5 | 98.33% | 96.69% | 95.08% | 59 | 98.3333 | 193.3889 | 83.7181 | 7.1312 | 59 | 0 | 4.9167 | 9.8333 | 14.75 | 19.6667 | 24.5833 | 29.5 | 34.4167 | 468.9681 | 464.1333 | 446.7283 | 435.125 | 412.8853 | 390.6456 | 362.6042 | 323.9264
58 | 3335 | 96.67% | 93.44% | 90.33% | 58 | 96.6667 | 186.8889 | 80.9043 | 6.7747 | 58 | 0 | 4.8333 | 9.6667 | 14.5 | 19.3333 | 24.1667 | 29 | 33.8333 | 453.2056 | 448.5333 | 431.7133 | 420.5 | 399.0078 | 377.5156 | 350.4167 | 313.0389
57 | 3277.5 | 95% | 90.25% | 85.74% | 57 | 95 | 180.5 | 78.1385 | 6.4303 | 57 | 0 | 4.75 | 9.5 | 14.25 | 19 | 23.75 | 28.5 | 33.25 | 437.7125 | 433.2 | 416.955 | 406.125 | 385.3675 | 364.61 | 338.4375 | 302.3375
56 | 3220 | 93.33% | 87.11% | 81.3% | 56 | 93.3333 | 174.2222 | 75.4209 | 6.0978 | 56 | 0 | 4.6667 | 9.3333 | 14 | 18.6667 | 23.3333 | 28 | 32.6667 | 422.4889 | 418.1333 | 402.4533 | 392 | 371.9644 | 351.9289 | 326.6667 | 291.8222
55 | 3162.5 | 91.67% | 84.03% | 77.03% | 55 | 91.6667 | 168.0556 | 72.7513 | 5.7769 | 55 | 0 | 4.5833 | 9.1667 | 13.75 | 18.3333 | 22.9167 | 27.5 | 32.0833 | 407.5347 | 403.3333 | 388.2083 | 378.125 | 358.7986 | 339.4722 | 315.1042 | 281.4931
54 | 3105 | 90% | 81% | 72.9% | 54 | 90 | 162 | 70.1299 | 5.4675 | 54 | 0 | 4.5 | 9 | 13.5 | 18 | 22.5 | 27 | 31.5 | 392.85 | 388.8 | 374.22 | 364.5 | 345.87 | 327.24 | 303.75 | 271.35
53 | 3047.5 | 88.33% | 78.03% | 68.92% | 53 | 88.3333 | 156.0556 | 67.5565 | 5.1693 | 53 | 0 | 4.4167 | 8.8333 | 13.25 | 17.6667 | 22.0833 | 26.5 | 30.9167 | 378.4347 | 374.5333 | 360.4883 | 351.125 | 333.1786 | 315.2322 | 292.6042 | 261.3931
52 | 2990 | 86.67% | 75.11% | 65.1% | 52 | 86.6667 | 150.2222 | 65.0313 | 4.8822 | 52 | 0 | 4.3333 | 8.6667 | 13 | 17.3333 | 21.6667 | 26 | 30.3333 | 364.2889 | 360.5333 | 347.0133 | 338 | 320.7244 | 303.4489 | 281.6667 | 251.6222
51 | 2932.5 | 85% | 72.25% | 61.41% | 51 | 85 | 144.5 | 62.5541 | 4.6059 | 51 | 0 | 4.25 | 8.5 | 12.75 | 17 | 21.25 | 25.5 | 29.75 | 350.4125 | 346.8 | 333.795 | 325.125 | 308.5075 | 291.89 | 270.9375 | 242.0375
50 | 2875 | 83.33% | 69.44% | 57.87% | 50 | 83.3333 | 138.8889 | 60.1251 | 4.3403 | 50 | 0 | 4.1667 | 8.3333 | 12.5 | 16.6667 | 20.8333 | 25 | 29.1667 | 336.8056 | 333.3333 | 320.8333 | 312.5 | 296.5278 | 280.5556 | 260.4167 | 232.6389
49 | 2817.5 | 81.67% | 66.69% | 54.47% | 49 | 81.6667 | 133.3889 | 57.7441 | 4.085 | 49 | 0 | 4.0833 | 8.1667 | 12.25 | 16.3333 | 20.4167 | 24.5 | 28.5833 | 323.4681 | 320.1333 | 308.1283 | 300.125 | 284.7853 | 269.4456 | 250.1042 | 223.4264
48 | 2760 | 80% | 64% | 51.2% | 48 | 80 | 128 | 55.4113 | 3.84 | 48 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 310.4 | 307.2 | 295.68 | 288 | 273.28 | 258.56 | 240 | 214.4
47 | 2702.5 | 78.33% | 61.36% | 48.07% | 47 | 78.3333 | 122.7222 | 53.1265 | 3.605 | 47 | 0 | 3.9167 | 7.8333 | 11.75 | 15.6667 | 19.5833 | 23.5 | 27.4167 | 297.6014 | 294.5333 | 283.4883 | 276.125 | 262.0119 | 247.8989 | 230.1042 | 205.5597
46 | 2645 | 76.67% | 58.78% | 45.06% | 46 | 76.6667 | 117.5556 | 50.8899 | 3.3797 | 46 | 0 | 3.8333 | 7.6667 | 11.5 | 15.3333 | 19.1667 | 23 | 26.8333 | 285.0722 | 282.1333 | 271.5533 | 264.5 | 250.9811 | 237.4622 | 220.4167 | 196.9056
45 | 2587.5 | 75% | 56.25% | 42.19% | 45 | 75 | 112.5 | 48.7013 | 3.1641 | 45 | 0 | 3.75 | 7.5 | 11.25 | 15 | 18.75 | 22.5 | 26.25 | 272.8125 | 270 | 259.875 | 253.125 | 240.1875 | 227.25 | 210.9375 | 188.4375
44 | 2530 | 73.33% | 53.78% | 39.44% | 44 | 73.3333 | 107.5556 | 46.5608 | 2.9578 | 44 | 0 | 3.6667 | 7.3333 | 11 | 14.6667 | 18.3333 | 22 | 25.6667 | 260.8222 | 258.1333 | 248.4533 | 242 | 229.6311 | 217.2622 | 201.6667 | 180.1556
43 | 2472.5 | 71.67% | 51.36% | 36.81% | 43 | 71.6667 | 102.7222 | 44.4685 | 2.7607 | 43 | 0 | 3.5833 | 7.1667 | 10.75 | 14.3333 | 17.9167 | 21.5 | 25.0833 | 249.1014 | 246.5333 | 237.2883 | 231.125 | 219.3119 | 207.4989 | 192.6042 | 172.0597
42 | 2415 | 70% | 49% | 34.3% | 42 | 70 | 98 | 42.4242 | 2.5725 | 42 | 0 | 3.5 | 7 | 10.5 | 14 | 17.5 | 21 | 24.5 | 237.65 | 235.2 | 226.38 | 220.5 | 209.23 | 197.96 | 183.75 | 164.15
41 | 2357.5 | 68.33% | 46.69% | 31.91% | 41 | 68.3333 | 93.3889 | 40.4281 | 2.3931 | 41 | 0 | 3.4167 | 6.8333 | 10.25 | 13.6667 | 17.0833 | 20.5 | 23.9167 | 226.4681 | 224.1333 | 215.7283 | 210.125 | 199.3853 | 188.6456 | 175.1042 | 156.4264
40 | 2300 | 66.67% | 44.44% | 29.63% | 40 | 66.6667 | 88.8889 | 38.48 | 2.2222 | 40 | 0 | 3.3333 | 6.6667 | 10 | 13.3333 | 16.6667 | 20 | 23.3333 | 215.5556 | 213.3333 | 205.3333 | 200 | 189.7778 | 179.5556 | 166.6667 | 148.8889
39 | 2242.5 | 65% | 42.25% | 27.46% | 39 | 65 | 84.5 | 36.5801 | 2.0597 | 39 | 0 | 3.25 | 6.5 | 9.75 | 13 | 16.25 | 19.5 | 22.75 | 204.9125 | 202.8 | 195.195 | 190.125 | 180.4075 | 170.69 | 158.4375 | 141.5375
38 | 2185 | 63.33% | 40.11% | 25.4% | 38 | 63.3333 | 80.2222 | 34.7282 | 1.9053 | 38 | 0 | 3.1667 | 6.3333 | 9.5 | 12.6667 | 15.8333 | 19 | 22.1667 | 194.5389 | 192.5333 | 185.3133 | 180.5 | 171.2744 | 162.0489 | 150.4167 | 134.3722
37 | 2127.5 | 61.67% | 38.03% | 23.45% | 37 | 61.6667 | 76.0556 | 32.9245 | 1.7588 | 37 | 0 | 3.0833 | 6.1667 | 9.25 | 12.3333 | 15.4167 | 18.5 | 21.5833 | 184.4347 | 182.5333 | 175.6883 | 171.125 | 162.3786 | 153.6322 | 142.6042 | 127.3931
36 | 2070 | 60% | 36% | 21.6% | 36 | 60 | 72 | 31.1688 | 1.62 | 36 | 0 | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 174.6 | 172.8 | 166.32 | 162 | 153.72 | 145.44 | 135 | 120.6
35 | 2012.5 | 58.33% | 34.03% | 19.85% | 35 | 58.3333 | 68.0556 | 29.4613 | 1.4887 | 35 | 0 | 2.9167 | 5.8333 | 8.75 | 11.6667 | 14.5833 | 17.5 | 20.4167 | 165.0347 | 163.3333 | 157.2083 | 153.125 | 145.2986 | 137.4722 | 127.6042 | 113.9931
34 | 1955 | 56.67% | 32.11% | 18.2% | 34 | 56.6667 | 64.2222 | 27.8018 | 1.3647 | 34 | 0 | 2.8333 | 5.6667 | 8.5 | 11.3333 | 14.1667 | 17 | 19.8333 | 155.7389 | 154.1333 | 148.3533 | 144.5 | 137.1144 | 129.7289 | 120.4167 | 107.5722
33 | 1897.5 | 55% | 30.25% | 16.64% | 33 | 55 | 60.5 | 26.1905 | 1.2478 | 33 | 0 | 2.75 | 5.5 | 8.25 | 11 | 13.75 | 16.5 | 19.25 | 146.7125 | 145.2 | 139.755 | 136.125 | 129.1675 | 122.21 | 113.4375 | 101.3375
32 | 1840 | 53.33% | 28.44% | 15.17% | 32 | 53.3333 | 56.8889 | 24.6272 | 1.1378 | 32 | 0 | 2.6667 | 5.3333 | 8 | 10.6667 | 13.3333 | 16 | 18.6667 | 137.9556 | 136.5333 | 131.4133 | 128 | 121.4578 | 114.9156 | 106.6667 | 95.2889
31 | 1782.5 | 51.67% | 26.69% | 13.79% | 31 | 51.6667 | 53.3889 | 23.1121 | 1.0344 | 31 | 0 | 2.5833 | 5.1667 | 7.75 | 10.3333 | 12.9167 | 15.5 | 18.0833 | 129.4681 | 128.1333 | 123.3283 | 120.125 | 113.9853 | 107.8456 | 100.1042 | 89.4264
30 | 1725 | 50% | 25% | 12.5% | 30 | 50 | 50 | 21.645 | 0.9375 | 30 | 0 | 2.5 | 5 | 7.5 | 10 | 12.5 | 15 | 17.5 | 121.25 | 120 | 115.5 | 112.5 | 106.75 | 101 | 93.75 | 83.75
[12 empty] | 100 | 77 | 58
INSTRUCTIONS:
| AFFINITY LAW CALCULATOR |  |  |  | SINGLE POINT CALCULATOR | [6 empty] | MULTIPOINT CALCULATOR
| Enter a motor speed for 60 Hz |  |  |  | The single point calculator allows entry of | [6 empty] | The multipoint calculator allows entry of up to eight, 60 Hz operating points in the row with the yellow background.
| operation in the cell with the |  |  |  | conditions from a single, 60Hz operating point | [6 empty] | Flow is entered beneath Q1 - Q8 and head is entered beneath H1 - H8. It is not necessary to begin with shutoff head
| yellow background and motor |  |  |  | on the pump curve into the cells with the yellow | [6 empty] | unless the pump will operate to the far left of the curve. Corresponding flows and heads are calculated for each point
| speeds at the lower frequencies |  |  |  | background. Flow, head (ft & psi), and HP are | [6 empty] | from 59 - 30 Hz (ie Q1 & H1, Q2 & H2, etc). The example included with the calculator shows flows of 0 - 140 GPM
| will be displayed. Note that the |  |  |  | calculated for each of the lower frequencies. | [6 empty] | and corresponding heads of 90' - 51' TDH. The "Auto Plot" function requires eight points to be entered for H & Q.
| affinity values do not change since | [10 empty] | If you have fewer than eight points the last point can be reentered several times. For example if you have only six points,
| they are a function of frequency, |  |  |  | The example included with the calculator | [6 empty] | reenter the values for Q6/H6 in both Q7/H7 and Q8/H8. The same will be true for the system curve.
| not 60hz motor speed. |  |  |  | has a 60 Hz design point of 100 GPM @ 200'
[5 empty] | and a power requirement of 7.5 BHP. | [6 empty] | To plot a system curve, enter the head values in SH1 through SH8. Auto Plot will automatically use the flows entered in
| The example included with the | [10 empty] | Q1 - Q8 for the X-axis values. The example shows a rising system curve due to increasing pipe friction above 250gpm.
calculator shows a 60 Hz motor
| speed of 3450 RPM. | [10 empty] | The multipoint calculator can also be used for engine drive pumps if you refer to column B (RPM) for the appropriate speed.
Although one can extract specific information from the table, a graphical representation is usually more useful. Click
on the Auto Plot Tabs (Feet & PSI) to view the chart. Autoplot automatically plots the 60, 55, 50, 45, 40, 35. & 30 hz curves
for the values entered in Q1 - Q8 and H1 - H8. Refer to the instructions below for custom plots.
Custom Plotting
The Chart Wizard is a bit particular about the order in which certain values are entered, so follow these instructions
closely to perform custom plots.
1) Click on and highlight the values of H1 - H8 for the first curve you wish to plot. For example, if you wish to plot the
60 Hz curve, highlight cells V22 - AC22.
2) Click on the Chart Wizard and select the XY-Scatter chart type. Select a chart sub-type that produces a true curve.
Usually they are the two in the middle. After selecting click "next". You should see a chart with a Y-axis of 0-400,
an X-axis of 0-10, and a smooth downward sloping curve.
3) Click on the "Series" tab. Click inside the "X-Values" box to locate your cursor there. Go back to the table and
highlight the 60 Hz values of Q1 - Q8 (cells N22 - T22). You should now see the proper flow points on the X-axis. Click
on the "Name" block and enter "60 Hz" to identify the curve.
4) To add another curve to the chart, click on "Add" in the lower left corner. Click on the "X-Values" box and then highlight
the next Q1 - Q8 series you wish to plot. (For example, highlight cells N32 - U32 to plot the 50 Hz curve). Clear the
contents of the "Y-Values" box and leave your cursor there. Highlight the corresponding H1 - H8 cells (in this case
V32 - AC32 for 50 Hz). You will now see two curves plotted on the same chart. Click on the "Name" box and enter
50 Hz to identify the curve. Continue adding curves in the same manner until you are finished. Then, click on "Next".
5) Enter a title for your chart and enter the descriptions you want for the X and Y axes. Click "Finished".
Your chart can now be printed, saved, or cut and pasted into other applications. If you selected a sub-chart type with "points"
on the curve, you will see the flow / head values when you cursor over them.
Do not fiddle with the cells below.
[19 empty] | 209.9567 | 207.7922 | 200 | 194.8052 | 184.8485 | 174.8918 | 162.3377 | 145.0216
[19 empty] | 176.422 | 174.6032 | 168.0556 | 163.6905 | 155.3241 | 146.9577 | 136.4087 | 121.8585
[19 empty] | 145.8033 | 144.3001 | 138.8889 | 135.2814 | 128.367 | 121.4526 | 112.7345 | 100.7095
[19 empty] | 118.1006 | 116.8831 | 112.5 | 109.5779 | 103.9773 | 98.3766 | 91.3149 | 81.5747
[19 empty] | 93.3141 | 92.3521 | 88.8889 | 86.5801 | 82.1549 | 77.7297 | 72.1501 | 64.4541
[19 empty] | 71.4436 | 70.7071 | 68.0556 | 66.2879 | 62.8998 | 59.5118 | 55.2399 | 49.3476
[19 empty] | 52.4892 | 51.9481 | 50 | 48.7013 | 46.2121 | 43.7229 | 40.5844 | 36.2554
[19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0